## Feuil1
Categories | Causes | Recommandation
Boiler Oxygene Corrosion | 1)Dissolved Oxygen: -Oxygen can dissolve in boiler water, especially during makeup water addition or blowdown. -Air leaks and inadequate deaeration of makeup water increase dissolved oxygen levels. 2)Electrochemical Corrosion: -Dissolved oxygen acts as an oxidizing agent, accelerating the corrosion of boiler metal components. 3)Pitting Corrosion: -Localized attack by dissolved oxygen can lead to pitting corrosion, weakening the boiler's structural integrity. 4)Oxygen Concentration Cells: -Variations in oxygen concentration within the boiler water can create areas of accelerated corrosion. | 1)Improve Deaeration: -Ensure efficient deaeration of the boiler makeup water to remove dissolved oxygen. -Maintain proper operation and maintenance of the deaerator system. 2)Use Oxygen Scavengers: -Introduce oxygen scavengers, such as sodium sulfite or hydrazine, into the boiler water. -These chemicals react with and remove the dissolved oxygen, preventing corrosion. 3)Maintain Boiler Water Chemistry: -Closely monitor and control the boiler water pH, alkalinity, and other chemical parameters to create a corrosion-resistant environment. -Adjust the water treatment program as needed to maintain optimal boiler water chemistry. 4)Inspect for Leaks and Deposits: -Regularly inspect the boiler and associated piping for any air leaks that could introduce oxygen into the system. -Remove any deposits or scale buildup that can create oxygen concentration cells and localized corrosion.
Bride de raccordement Clogged due scale and TH value | Water systems with high mineral content or hardness | Cheek the water quality (softner …..)
Combusion chamber Cologged due bad combustion | 1)Incomplete Combustion: -Improper air-fuel ratio in the burner, leading to incomplete burning of the fuel. -Insufficient air supply or poor air distribution in the combustion chamber. 2)Fuel Quality Issues: -Use of low-quality or contaminated fuel, resulting in incomplete combustion and the formation of combustion byproducts. -Improper fuel atomization or mixing with air. 3)Burner Maintenance Issues: -Worn or malfunctioning burner components, such as nozzles, ignition systems, or controls, affecting the combustion process. -Improper burner adjustments or settings. 4)Fouling and Deposits: -Accumulation of soot, ash, or other combustion byproducts on the combustion chamber walls and surfaces. -Buildup of scale or deposits on the heat transfer surfaces, reducing heat transfer efficiency. | 1)Optimize Combustion: -Adjust the air-fuel ratio to achieve complete and efficient combustion. -Ensure proper air supply and distribution in the combustion chamber. -Regularly clean and maintain the burner components to ensure optimal performance. 2)Improve Fuel Quality and Handling: -Use high-quality, clean fuel that meets the boiler manufacturer's specifications. -Implement proper fuel storage, handling, and filtration to minimize contamination. -Ensure proper fuel atomization and mixing with air. 3)Implement Regular Maintenance: -Perform scheduled cleaning and inspection of the combustion chamber, heat transfer surfaces, and burner components. -Replace worn or malfunctioning parts as needed to maintain optimal combustion efficiency. -Adjust the burner settings and controls according to the manufacturer's recommendations.
Conductivity Sensor Clogged with scale | A conductivity sensor can become clogged with scale build up over time, especially in water systems with high mineral content or hardness. The scale deposits on the sensor's electrodes or measurement surfaces, preventing accurate conductivity readings. | To address a conductivity sensor clogged with scale, the following steps are recommended: 1)Clean the sensor: -Carefully remove the sensor from the measurement location. -Use a mild acid solution (e.g., diluted vinegar or citric acid) to dissolve and remove the scale buildup on the sensor's surfaces. -Gently scrub the sensor with a soft-bristled brush or a non-abrasive cleaning pad to dislodge any remaining scale. -Rinse the sensor thoroughly with clean water to remove any residual cleaning solution. 2)Inspect the sensor: -Examine the sensor for any physical damage or wear, such as pitting, corrosion, or cracked surfaces. If the sensor is damaged, it may need to be replaced. 3)Preventive maintenance: -Consider installing water softeners or filters to reduce the mineral content in the water, which can help prevent future scale buildup. Establish a regular cleaning schedule for the conductivity sensor, depending on the water quality and operating conditions. -Use appropriate sensor materials (e.g., stainless steel, Hastelloy) that are resistant to scale formation in your specific water system. 4)Calibrate the sensor: After cleaning and reinstalling the sensor, calibrate it according to the manufacturer's instructions to ensure accurate conductivity readings.
Conductivity Sensor in normal condition | water quality can be respected | 1)Improve
Deasalting Valve in normal condition | water quality can be respected | 1)Improve boiler maintenance:
Flame tube Clogged by scale due to TH | High Total Hardness (TH): Total Hardness refers to the concentration of calcium and magnesium ions in the water. When the TH is High, these minerals can precipitate and form scale deposits on the flame tube and other boiler components. -Improper water treatment: Inadequate water treatment or lack of a proper water softening system can lead to the accumulation of scale-forming minerals in the boiler water. | 1)Improve water treatment: -Install a water softening system: A water softener can effectively remove the calcium and magnesium ions from the water, reducing the formation of scale. -Implement a chemical water treatment program: Use appropriate water treatment chemicals, such as scale inhibitors or dispersants, to prevent the precipitation of scale-forming minerals. -Regularly test and monitor the water quality: Regularly check the TH and other water parameters to ensure the water treatment system is working effectively. 2)Clean the flame tube: -Shut down the boiler and allow it to cool completely before attempting any maintenance. -Carefully remove the flame tube and inspect it for scale buildup. -Use a mechanical cleaning method, such as wire brushing or high-pressure water flushing, to remove the scale deposits. -Avoid using harsh chemicals or abrasives, as they can damage the flame tube. 3)Improve boiler maintenance: -Establish a regular boiler maintenance schedule to inspect and clean the flame tube and other critical components. -Regularly check and clean the boiler's water-side surfaces to prevent the accumulation of scale. -Consider installing a boiler blowdown system to periodically remove a portion of the boiler water, which can help flush out dissolved minerals and prevent scale buildup. 4)Consider upgrading the boiler system: If the scale buildup is severe and persistent, it may be necessary to upgrade the boiler system, including the water treatment equipment, to better handle the water quality issues.
Fuel Liquide in burner side | 1)Incomplete Combustion: -Improper air-fuel ratio in the burner, leading to incomplete burning of the fuel. -Insufficient air supply or poor air distribution in the combustion chamber. 2)Fuel Quality Issues: -Use of low-quality or contaminated fuel, resulting in incomplete combustion and the formation of combustion byproducts. -Improper fuel atomization or mixing with air. -Check fioul temprerature 3)Burner Maintenance Issues: -Worn or malfunctioning burner components, such as nozzles, ignition systems, or controls, affecting the combustion process. -Improper burner adjustments or settings. | 1)Optimize Combustion: -Adjust the air-fuel ratio to achieve complete and efficient combustion. -Ensure proper air supply and distribution in the combustion chamber. -Regularly clean and maintain the burner components to ensure optimal performance. 2)Improve Fuel Quality and Handling: -Use high-quality, clean fuel that meets the boiler manufacturer's specifications. -Implement proper fuel storage, handling, and filtration to minimize contamination. -Ensure proper fuel atomization and mixing with air. 3)Implement Regular Maintenance: -Perform scheduled cleaning and inspection of the combustion chamber, heat transfer surfaces, and burner components. -Replace worn or malfunctioning parts as needed to maintain optimal combustion efficiency. -Adjust the burner settings and controls according to the manufacturer's recommendations.
Furnace corroded due to Dissolved Gases Oxygene and carbon | 1)Oxygen Corrosion: Oxygen can enter the furnace system through various sources, such as air leaks, improper venting, or the use of makeup water. Oxygen can react with the metal components of the furnace, leading to oxidation and the formation of rust and other corrosive byproducts. 2)Carbon Dioxide Corrosion: Carbon dioxide (CO2) can dissolve in the furnace water, forming carbonic acid (H2CO3). This acidic environment can accelerate the corrosion of metal components, including the heat exchanger, piping, and other furnace parts. | 1)Eliminate Oxygen Ingress: -Inspect the furnace for any air leaks and seal them properly to prevent the introduction of oxygen. -Ensure proper venting of the furnace to allow for the safe and efficient removal of combustion byproducts. -Use deaerated or deoxygenated makeup water to replenish the furnace system. 2)Implement Water Treatment: -Install a water softener or a reverse osmosis system to remove dissolved minerals and reduce the potential for scale formation. -Use a chemical water treatment program that includes corrosion inhibitors and pH buffers to maintain the water's pH within the optimal range. -Consider adding an oxygen scavenger or a degassing system to remove dissolved oxygen from the furnace water. 3)Perform Regular Maintenance: -Regularly inspect the furnace for signs of corrosion, such as rust, pitting, or leaks. -Clean and flush the furnace system to remove any accumulated sludge or debris that can contribute to corrosion. -Replace any severely corroded components to prevent further damage and ensure the furnace's safe and efficient operation.
Level Indicator damaged due to corrosion and hight PH | 1)Corrosion: Corrosion of the level indicator components can be caused by exposure to corrosive environments, such as aggressive fluids or gases. The construction materials of the level indicator may not be suitable for the operating conditions, leading to premature degradation. 2)High pH: Excessively high (alkaline) pH of the water or fluid can also contribute to the corrosion of the level indicator materials. High pH can attack and degrade the protective coatings, seals, and metallic components of the indicator. | 1)Water treatment: -Implement a water treatment system to adjust the pH us recommanded -Use appropriate corrosion inhibitors to protect the level indicator components. -Ensure that water used are free of contaminants that can accelerate corrosion. 2)Regular monitoring and maintenance: -Regularly inspect the level indicator for signs of corrosion or damage. -Perform preventive maintenance, such as cleaning, lubrication, and replacement of worn parts. 3)Consider replacement: If the damage caused by corrosion and high pH is too severe, it may be necessary to replace the level indicator and boiler water side inspect.
Level Indicator in normal condition | good | igood
Level Probe Clogged | 1)Mineral Buildup: -In steam boilers, the high temperatures and evaporation of water can lead to the precipitation of dissolved minerals, such as calcium, magnesium, and silica. -These minerals can accumulate on the level probe, forming a scale or sludge buildup that obstructs the probe's function. 2)Carryover of Boiler Water: -Excessive foaming or carryover of boiler water can occur due to high concentrations of dissolved solids, improper water treatment, or excessive boiler loading. -The entrained water droplets and suspended solids can deposit on the level probe, causing it to become clogged. | 1)Improve Water Treatment: -Implement a comprehensive water treatment program to control the concentration of dissolved minerals and prevent scale formation. -Use water softeners, demineralizers, or reverse osmosis systems to reduce the hardness and total dissolved solids (TDS) in the boiler water. -Regularly test and monitor the boiler water quality to ensure the effectiveness of the water treatment system. 2)Optimize Boiler Blowdown: -Establish a proper boiler blowdown routine to remove a portion of the high-solids boiler water and replenish it with fresh, treated water. -Adjust the blowdown rate based on the boiler water TDS levels to maintain them within the recommended range. 3)Clean and Maintain the Level Probe: -Regularly inspect the level probe for signs of clogging or buildup and clean it as necessary. -Use a soft-bristle brush, mild acid solutions, or ultrasonic cleaning methods to remove any deposits from the probe. -Avoid using abrasive or harsh cleaning methods that could damage the probe. 4)Implement Continuous Monitoring:
Level Probe in normal condition | hyj | vv
Low low Level electrode Clogged and corroded | 1)Mineral Buildup: -The high temperatures and constant evaporation of water in a steam boiler can lead to the precipitation of dissolved minerals, such as calcium, magnesium, and silica. -These minerals can accumulate on the low-low level electrode, forming a scale or sludge buildup that obstructs the electrode's function. 2)Corrosion: -The aggressive environment of the steam boiler, with its high temperatures, pressures, and potentially corrosive water chemistry, can cause the corrosion of the low-low level electrode materials. -Factors like water pH, dissolved oxygen, and the presence of chlorides or other corrosive ions can accelerate the corrosion process. -Corrosion can degrade the electrode's surface, leading to a loss of conductivity and clogging. 3)Carryover of Boiler Water: -Excessive foaming or carryover of boiler water can occur due to high concentrations of dissolved solids, improper water treatment, or excessive boiler loading. -The entrained water droplets and suspended solids can deposit on the low-low level electrode, causing it to become clogged. | 1)Improve Water Treatment: -Implement a comprehensive water treatment program to control the concentration of dissolved minerals and prevent scale formation. -Use water softeners, demineralizers, or reverse osmosis systems to reduce the hardness and total dissolved solids (TDS) in the boiler water. -Regularly test and monitor the boiler water quality to ensure the effectiveness of the water treatment system. 2)Optimize Boiler Blowdown: -Establish a proper boiler blowdown routine to remove a portion of the high-solids boiler water and replenish it with fresh, treated water. -Adjust the blowdown rate based on the boiler water TDS levels to maintain them within the recommended range. 3)Clean and Maintain the Low-Low Level Electrode: -Regularly inspect the low-low level electrode for signs of clogging or corrosion and clean it as necessary. -Use a soft-bristle brush, mild acid solutions, or ultrasonic cleaning methods to remove any deposits from the electrode. -Avoid using abrasive or harsh cleaning methods that could further damage the electrode.
Low low Level electrode in normal condition | jre | increase chimical product
PT100 Clogged and corroded | yy | vdh
PT100 in a normal condition | yt | increase chimical product
Safety valve in normal condition | ytt | increase chimical product
Valve Corroded | 1)Corrosion: -The aggressive environment of the steam boiler, with its high temperatures, pressures, and potentially corrosive water chemistry, can cause the corrosion of the Valve materials. -Factors like water pH, dissolved oxygen, and the presence of chlorides or other corrosive ions can accelerate the corrosion process. -Corrosion can degrade the valve's surface, leading to a loss of conductivity and clogging. | 1)Improve Water Treatment: -Implement a comprehensive water treatment program to control the concentration of dissolved minerals and prevent scale formation. -Use water softeners, demineralizers, or reverse osmosis systems to reduce the hardness and total dissolved solids (TDS) in the boiler water. -Regularly test and monitor the boiler water quality to ensure the effectiveness of the water treatment system. -Control retun condensat quality